# Sliding Watertight Barrier (WK Model# FG-S) Specifications

## Part 1 – General

  - Description: Provide sliding P-Curl gasket barrier(s) factory assembled with frame(s) and hardware in accordance with contract specifications and approved drawings.

  - Acceptable Manufacturers: Sliding barrier shall be as manufactured by Walz & Krenzer, Inc

  - Acceptable Distributor: Flood gate to be distributed by Floodproofing.com (1-800-507-0865; info@floodproofing.com)

  - Standards: Comply with the provisions of the following (as applicable):

- AISC “Specifications for Design, Fabrication, and Erection of Structural Steel for Buildings”.

- The Aluminum Assoc. “Aluminum Design Manual”.

- AWS Structural Welding Code D1.1, D1.2, D1.3, D1.6.

- ASME Structural Welding Code Section IX.

- FEMA Bulletin 3-93, #102 & #114.

  - Submittals:

- Manufacturers Data: Submit installation and maintenance manuals for flood barrier.

- Shop Drawings: Submit shop drawings approved by licensed Professional Engineer for flood barrier including dimensional plans, elevations, sections, details for all mountings/connections, and parts list.

- Calculations (optional for critical applications): Submit calculations approved by licensed Professional Engineer verifying the flood barrier’s ability to withstand the design pressure loading.

- QA Submittals: Submit test reports showing compliance with specified performance characteristics.

  - Qualifications: Manufacturer shall present evidence attesting to at least ten years successful experience in the design and manufacture of similar closures.

## Part 2 – Products

- Product Description: Sliding barrier shall be Model FG-S as manufactured by Walz & Krenzer, Inc.

- Materials:

- Panel: ASTM A-36/ASTM A572 Gr 50 mild steel, 304/316 stainless steel, or 6061-T6 aluminum

- Frame: ASTM A-36 steel or 304/316 stainless steel

- Latches (if required): stainless steel latch bolts.

- Gasket: Walz & Krenzer P-Curl gasket made from EPDM with fully-molded straight sections (no extrusions permitted) and fully-molded corners. All joints shall be fully vulcanized. Bottom frame to side frame transition shall have a suitable radius to ensure proper seal.

- Fence Mechanisms: ASTM A-36 mild steel or stainless steel.

- Guide Rails: ASTM A-36 mild steel or stainless steel.

- Finish: steel or aluminum panels and frames to be coated with (1) primer coat and (2) top coats of shop polyurethane system. Stainless steel to be uniform bead blast per SSPC-SP17 (other options available upon request).

- Design:

- Design Pressure: # (in feet of water or psi). Specify seating (pushing gate closed) or unseating direction (pushing gate open).

- Gasket shall be retracted to prevent dragging on frame and sill surfaces when the panel is moving.

- Sill plate shall be flush with no trough in ground permitted.

- Walz & Krenzer P-Curl gasket shall be deployed using fence mechanisms around seal perimeter. Fences can be either manually deployed or in a “quick-acting” mechanism.

- For large gates, winch assemblies (manual or electrical) with wire rope can be supplied to open and close the gate.

- Panels can be designed to roll along floor or hang from track mounted to wall/ceiling.

- Installation:

  - Frame(s) shall have mounting holes for expansion or adhesive concrete anchors for installation on existing openings.

  - For new concrete pours, frame(s) shall have welded embedment anchors and/or a masonry subframe.

  - Other options included weld-on installation (field welding by installer).

- Additional requirements such as hydrodynamic loads, impact loads and breaking wave loads shall be added as required by the specific application.

- Quality Assurance:

- Perform shop dimensional & flatness tests.

- Perform shop chalk test.

- All welding shall be performed in accordance with the requirements of the applicable AWS or ASME standards.

- Non-Destructive Testing (if required) options include:

  - Liquid Penetrant Test: Welds in the “potential” leak path shall be liquid penetrant inspected in accordance with Appendix VIII of Section VIII of ASME Code Div. 1.

  - Magnetic Particle Testing (MT) available for non-stainless steel.

  - Other tests are available upon request.

- Hydrostatic Test (if required): Provide hydrostatic test data certifying that the closure furnished, or a closure of similar design, has been satisfactorily tested to verify that it will withstand the designed hydrostatic pressure with no visible leakage. Available upon request.

# Part 3 – Execution

- Fabrication:

- The finished product shall be rigid, neat in appearance, and free from all defects, warps, and buckles.  All exposed joints and corners shall be well rounded.

- All welding shall be performed in accordance with the requirements of the applicable AWS or ASME standards.

- The panel gasket channel and frame knife edge shall be flat within 1/16” in any 6’ length.

- All butt welds to be full penetration welds.

- Installation:

- Install flood barrier in accordance with manufacturer’s instructions and approved shop drawings.

- After installation, perform field operational test per manufacturer’s instructions to verify seal.

- Finish paint (if applicable) after installation.

- Warranty: Sliding barrier shall operate satisfactorily and be free of defects in material and workmanship for a period of not less than one year from the date of delivery.